The Ohio State University requires a Fire Protection Impairment Plan before doing any work that will impact the building’s fire protection system(s).  The Fire Protection Impairment Plan is required to ensure the safe shutdown of fire protection system(s), control potential fire hazards during the impairment, and minimize the duration of the impairment by reinstating the fire protection system as soon as possible.

An impairment occurs when a fire protection or detection system, fire alarm system or other system designated to maintain the fire resistance of the building element or structure is taken out of service, either wholly or in part, planned or unplanned. Fire protection or detection equipment subject to impairment management includes automatic sprinkler systems, fire protection water supplies, fire pumps, fire mains, gas extinguishing systems, foam systems, fire detection systems, water mist systems, powder systems, explosion suppression systems, fire doors, walls, ceilings, etc.

Directions

Complete the form, print, and initial where indicated. Sign the last page, scan, and save as a file, and e-mail the completed document to emergencymanagement@osu.edu.

The form will be reviewed and an e-mail sent indicating if the form was accepted or rejected. Once accepted, random inspection(s) will be made to monitor compliance with the impairment plan. If violations of the plan are noted during these inspections, construction will be halted until all violations have been corrected.

| Job Site |
| --- |
| Building Name & Number | Impairment Dates |
| Street Address & Zip | # Stories Above Grade | # Stories Below Grade |
| Unit, Suite, Floor | Gross Sq.Ft. Working Area |
| Construction Type | Use Group |
| Existing Use of Building Space | Describe Project, Work |
| Describe Steps Being Taken to Address Impacted Systems | Describe Steps Being Taken if Impairment Exceeds Planned Time Frame |

| Plan Acknowledgment |
| --- |
| Contractor Company | Contact Person |
| Address | Telephone | Fax |
| City, State, Zip | Email |
| By initialing the items below, the Project Manager certifies that the Fire Protection Impairment Plan complies with the following criteria: |
| _____ | 1. The impairment plan complies with the applicable edition of the (OFC) Ohio Fire Code 1301:7-7-09(A)(7)901.7, 1301:7-7-33(H)(6) 3308.6, and NFPA 241. |
| _____ | 2. Where a required fire protection system is out of service, The Ohio State University, Communications & Security Technology Division (614-292-6677) and Emergency Management & Fire Prevention Division shall be notified immediately and an approved fire watch, or other approved method, shall be provided until the fire protection system has been returnead to service [OFC 1301:7-7-09(A)(8)901.8]. This includes system shut-down and removals in suppressed areas. |
| _____ | 3. The Project Manager or their designee shall assign an impairment coordinator to comply with the requirements of the code. In the absence of a specific impairment coordinator, the Project Manager shall be considered the impairment coordinator. [OFC 1301:7-7-09(A)(7)(a)901.7.1] |
| _____ | 4. A tag shall be used to indicate that a system, or portion thereof, has been removed from service. [OFC 1301:7-7-09(A)(7)(b)901.7.2] |
| _____ | 5. The tag shall be posted at each fire department and standpipe connection, system control valve, fire alarm control panel (FACP), fire alarm annunciator panel (FAAP) and fire command center, indicating which system, or part thereof, has been removed from service. [OFC 1301:7-7-09(A)(7)(c)901.7.3] |
| _____ | 6. Preplanned impairments must be authorized by The Ohio State University Fire Prevention Director or his designee. Before authorization is given, the Project Manager or their designee shall be responsible for verifying that all of the following procedures have been implemented. [OFC 1301:7-7-09(A)(7)(d)901.7.4] The extent and expected duration of the impairment have been determined. The areas or buildings involved have been inspected and the increased risks determined. The Ohio State University Insurance Administrator, The Ohio State University Department of Public Safety Communications & Security Technology Division, building coordinator and building leadership/management, and Emergency Management & Fire Prevention Director or his designee have been notified. The building coordinator and building leadership/management in the areas to be affected have been notified. A tag impairment system has been implemented. Necessary tools and materials have been assembled on the impairment site. |
| _____ | 7. When impaired equipment is restored to normal working order, the impairment coordinator shall verify that all of the following procedures have been implemented [OFC 1301:7-7-09(A)(7)(f)901.7.6]: Necessary inspections and tests have been conducted to verify that affected systems are operational. Building coordinator and building leadership/management have been advised that protection is restored. The Ohio State University Fire Prevention Director or his designee has been advised that protection is restored. The Ohio State University Insurance Administrator and other involved parties have been advised that protection is restored. The impairment tags have been removed. |
| _____ | 8. A copy of the fire protection Impairment plan, all system impairment permit(s), fire watch logs, and associated documents shall be kept at the job site, in a 3-RING BINDER. |

| Project Manager |
| --- |
| Company | Contact Person |
| Address | Telephone | Fax |
| City, State, Zip | Email |

| Acknowledgment |
| --- |
| Any system that is out of service shall be reported to The Ohio State University, Department of Public Safety, Emergency Management & Fire Prevention Division (EMFP). A system being placed “on test” and still in-service, while sprinkler or alarm contractor(s) are on-site, does not have to be reported to EMFP. I understand that if I need assistance developing a risk mitigation plan I may contact The Ohio State University, Department of Public Safety, Emergency Management & Fire Prevention Division (EMFP) at 614-247-4911, emergencymanagement@osu.edu. I understand that I can discuss the parameters of a fire watch or seek approval to perform a fire watch by contacting The Ohio State University, Department of Public Safety, Emergency Management & Fire Prevention Division (EMFP) at 614-247-4911, emergencymanagement@osu.edu I understand that this acknowledgment is important, and I have told the truth on it and all attached papers. |
| Date | Name | Signature |